## Equipment
Appendix 2A GWA Water Booster Stations - Equipment
ADDED: Santa Ana Upper, Lower, Malojloj Elevated, Line Booster
|  |  |  | Condition and Functionality Rating | [9 empty] | Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor - Motor | [15 empty] | Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment - Driven Equipment
Booster Station | Equipment Name | Asset Class | Asset Number | Physical Condition Rating |  |  |  |  | Functionality Rating |  |  |  |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Temperature |  | High Efficiency |  | Power Factor Correction |  | Runtime | Bases |  |  |  | Mean Time Between Failure |  |  | Vibration |  | Cavitation |  | Temperature |  | Pump Performing |  | Seals Functional |  | Seal Water System Functional
|  |  |  | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Hours | 0 | 1 | 2 | 3 | 1 | 2 | 3 | Excessive | Normal | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Yes | No
Agana Heights (Ulloa Untalan) | under litigation (private property, could not evaluate)
centrifugal pump above ground, 50 gal surge tank, pressure switch
Agat/Umatac (Umatac #1)
| Pump | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | manual on/off, based on level in tank | bar: Physical Condition Rating 3; Functionality Rating 3
Santa Ana Upper | Pump 1 | [25 empty] | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  | x
| Pump 2 | [12 empty] | na |  |  |  | x |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x |  | x | na |  | turbine pump, leaks | bar: Physical Condition Rating 2; Functionality Rating 3
[14 empty] | na |  |  |  | x |  | x |  |  | na |  | na | [24 empty] | room for 3rd pump, never installed | bar: Physical Condition Rating 0; Functionality Rating 1
Santa Ana Lower
| Pump | [12 empty] | na | x |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  | x |  | new seals | bar: Physical Condition Rating 2; Functionality Rating 3
Asan Spring | SECURED due to fecal count in spring
| Pump 1 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  | x |  | spot for 3rd pump | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 2 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
| CL2 system | [12 empty] | na |  |  | x |  |  |  | x |  | na |  | na |  | na |  | na | na |  |  | na |  |  | na |  |  | na |  | na |  | na | x |  | na |  | na | bar: Physical Condition Rating 2; Functionality Rating 2
Barrigada
| Pump 1 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 4; Functionality Rating 4
| Pump 2 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | newly rebuilt | bar: Physical Condition Rating 3; Functionality Rating 3
Chalan Palauan | [49 empty] | No Cl2 facilities; no genset; safety issues
| Pump 1 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | new pump/motor | bar: Physical Condition Rating 4; Functionality Rating 4
| Pump 2 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | new pump/motor | bar: Physical Condition Rating 4; Functionality Rating 4
| Pump 3 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | new pump/motor | bar: Physical Condition Rating 4; Functionality Rating 4
| Pump 4 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | new pump/motor | bar: Physical Condition Rating 4; Functionality Rating 4
Mangenon Access Road
| Pump 1 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  |  | x | x | bar: Physical Condition Rating 2; Functionality Rating 3
| Pump 2 | [12 empty] | na |  |  | x |  |  | x |  |  | na |  | na |  | x |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x | x |  | x | bar: Physical Condition Rating 2; Functionality Rating 1
| Pump 3 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x | x |  |  | x | na |  |  |  | x |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 2; Functionality Rating 3
Pago Bay
| Pump 1 | [12 empty] | na |  |  | x |  |  | x |  |  | x | x |  |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x | x |  | x |  |  | x | x |  | seals need replacing, no guard coupling | bar: Physical Condition Rating 2; Functionality Rating 2
| Pump 2 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | rebuilt recently | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 3 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  | x |  | bearing problem, no coupling guard | bar: Physical Condition Rating 2; Functionality Rating 2
Ugum
| Pump | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x | x |  |  | x | x |  | x |  | x | bar: Physical Condition Rating 2; Functionality Rating 2
Northern | at WWTP - did not assess
Wusstig | abandoned
Malojloj (Malojloj Elevated)
| Pump 1 | [16 empty] | x |  |  | x |  | x |  | x |  | x |  | x | na |  |  |  | x |  | x |  |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 2 | [16 empty] | x |  |  | x |  | x |  | x |  | x |  | x | na |  |  |  | x |  | x |  |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 3 | [16 empty] | x |  |  | na |  | na |  | na |  | na |  | na | na |  |  |  | x |  | na |  |  | na |  | na |  | na |  | x | na |  | na | bar: Physical Condition Rating 0; Functionality Rating 0
Malojloj Line Booster
| Pump 1 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x | x |  |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x |  | na |  | na | all new seals, all motors rewound, all new impellers | bar: Physical Condition Rating 4; Functionality Rating 4
| Pump 2 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x | x |  |  | x | na |  |  |  | x |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 4; Functionality Rating 4
| Pump 3 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x | x |  |  | x | na |  |  |  | x |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 4; Functionality Rating 4
Latte Heights
| Pump 1 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x |  | x |  | x | na |  |  |  | x |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | all pumps rebuilt recently | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 2 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x |  | x |  | x | na |  |  |  | x |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 3 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x |  | x |  | x | na |  |  |  | x |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
Lower Pigua (Gayos)
| Pump | [12 empty] | na |  | x |  |  |  |  | x |  | x |  | x | x |  |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | seals new, motor rewound, poor coatings, space for 3 pumps but only 1 | bar: Physical Condition Rating 1; Functionality Rating 2
Toguan (Umatac #3)
| Pump 1 | [12 empty] | na |  |  | x |  | x |  |  |  | x | x |  |  | x |  | x | na |  |  | x |  | x |  |  | x |  | x |  |  | x | x |  |  | x |  | x | leaking | bar: Physical Condition Rating 1; Functionality Rating 2
| Pump 2 | [12 empty] | na |  |  | x |  | x |  |  |  | x |  | x |  | x |  | x | na |  |  | x |  | x |  |  |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 2
Upper Pigua (Pigua)
| Pump 1 | [15 empty] | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 2 | [15 empty] | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
Adawag
| Pump | [15 empty] | x |  |  |  | x |  | x | x |  |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x | x |  | x |  | x |  | x |  | above ground centrifugal pump, running hot, water line above ground level | bar: Physical Condition Rating 3; Functionality Rating 3
Lower Nimitz Hill
| Pump 1 | [14 empty] | x |  |  |  |  | x |  | x | x |  | x |  |  | x | na |  |  |  | x |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | both pumps new, running hot, on timers (6 hr rotation) | bar: Physical Condition Rating 4; Functionality Rating 4
| Pump 2 | [14 empty] | x |  |  |  |  | x |  | x | x |  | x |  |  | x | na |  |  |  | x |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | pipes unpainted | bar: Physical Condition Rating 4; Functionality Rating 4
Upper Nimitz Hill
SECURED
Santa Rita
| Pump 1 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 4; Functionality Rating 4
| Pump 2 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 4; Functionality Rating 4
| CL2 Scale | [12 empty] | na | [15 empty] | na | bar: Physical Condition Rating 2; Functionality Rating 1
| CL2 ejector | [12 empty] | na | [15 empty] | na | bar: Physical Condition Rating 3; Functionality Rating 2
| CL2 Pump | [12 empty] | na | x | [14 empty] | na | x | bar: Physical Condition Rating 2; Functionality Rating 2
Sinifa | converted to prv - did not visit
Truman | [49 empty] | space for 3 pumps, but only 2
| Pump 1 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  |  | x |  | x | motor rewound (cond 2), wires exposed | bar: Physical Condition Rating 2; Functionality Rating 3
| Pump 2 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  |  | x |  | x | motor rewound (cond 3) | bar: Physical Condition Rating 2; Functionality Rating 3
Sinijana (Pale Kirin)
| Pump | [12 empty] | na |  |  |  | x |  | x |  |  | x |  | x |  | x |  | x | na |  |  |  | x |  | x |  |  | x |  | x |  | x | x |  | x |  | x |  | above ground centrifugal pump, operates on pressure switch | bar: Physical Condition Rating 3; Functionality Rating 3
| 50 gal tank | [12 empty] | na |  |  |  | x | [15 empty] | x |  | x | [7 empty] | x |  | na | bar: Physical Condition Rating 3; Functionality Rating 3
Umatac #1 | See above Agat/Umatac
Umatac #2
| Pump 1 | [12 empty] | na | [5 empty] | x |  |  | na |  | na |  | x |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na | x |  | na |  |  | x | out | bar: Physical Condition Rating 0; Functionality Rating 0
| Pump 2 | [12 empty] | 0 |  | x |  |  |  |  | x |  | na |  | na | x |  |  | x | 0 |  |  |  | x |  |  | x |  | na |  | na |  | na | x |  | na |  |  | x | needs to be anchored | bar: Physical Condition Rating 4 to Functionality Rating 0
| Temporary Pump | [12 empty] | na |  | x |  |  |  | na |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | na |  |  | x |  | x |  | x |  | x | x |  | x |  | temporary pump until Pump 2 anchored and new pump installed | bar: Physical Condition Rating 3; Functionality Rating 3
Umatac #3 | See above Toguan
Gayinero
| Pump 1 | [12 empty] | na |  | x |  |  | x |  |  |  | na |  | na |  | x |  | x | na |  |  | x |  | x |  |  |  | na |  | na |  | na |  | x | na |  | x | bar: Physical Condition Rating 0; Functionality Rating 0
| Pump 2 | [12 empty] | na |  | x |  |  | x |  |  |  | x | x |  |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 2; Functionality Rating 2
Mataguac
| Pump 1 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x | x |  |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 2 | [12 empty] | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x | na |  | x | bar: Physical Condition Rating 0; Functionality Rating 0
| Pump 3 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x | x |  |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | new | bar: Physical Condition Rating 3; Functionality Rating 3
| cl2 feed pump 1 | [12 empty] | na |  |  | na |  |  |  | x |  | x |  | na |  | na |  | x | na |  |  | na |  |  |  | x |  | na |  | na |  | na |  | x | x |  | x |  | both cl2 pumps new never used, cl2 tank present but not used (good residual already), chlorinators missing | bar: Physical Condition Rating 3; Functionality Rating 3
| cl2 feed pump 2 | [12 empty] | na |  |  | na |  |  |  | x |  | x |  | na |  | na |  | x | na |  |  | na |  |  |  | x |  | na |  | na |  | na |  | x | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
Santa Rosa
| Pump 1 | [12 empty] | na |  |  | x |  |  | x |  | na |  | ns |  |  | x |  | x | na |  |  | x |  |  | x |  |  | na |  | na |  | na |  | x | na |  | x | bar: Physical Condition Rating 0; Functionality Rating 0
| Pump 2 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
Yigo Elevated Tank
| Pump 1 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x | x |  |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | new, one pump normally in use, alternates | bar: Physical Condition Rating 4; Functionality Rating 4
| Pump 2 | [12 empty] | na |  |  | x |  | x |  |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  | x |  | new seals and impeller | bar: Physical Condition Rating 3; Functionality Rating 3
Brigade
| Pump 1 | [12 empty] | na |  |  |  | x |  | x |  |  | x |  | x |  | x |  | x | na |  |  |  | x |  | x |  |  | x |  | x |  | x | x |  |  | x | x |  | seals poor, some leakage | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 2 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x |  | x |  | x | na |  |  |  | x |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | seals new | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 3 | [12 empty] | na |  |  |  | x |  |  | x |  | x |  | x |  | x |  | x | na |  |  |  | x |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | seals new | bar: Physical Condition Rating 2; Functionality Rating 2
Camacho's
| Pump | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  |  | x | impeller good, seals good, centrifugal pump | bar: Physical Condition Rating 2; Functionality Rating 3
Windward Hills
| Pump 1 | [12 empty] | na |  |  | x |  |  |  | x |  | x |  | x |  | x |  | x | na |  |  | x |  |  |  | x |  | x |  | x |  | x | x |  | x |  | x |  | pump new, motor rewound | bar: Physical Condition Rating 3; Functionality Rating 3
| Pump 2 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  | x |  | removed new motor | bar: Physical Condition Rating 3; Functionality Rating 0
| Pump 3 | [12 empty] | na |  |  | x |  |  | x |  |  | x |  | x |  | x |  | x | na |  |  | x |  |  | x |  |  | x |  | x |  | x | x |  | x |  | x |  | motor rewound | bar: Physical Condition Rating 2; Functionality Rating 2
Yona | SECURED
Note on A29: Kalani, I had 4 pumps in my notes-all new? I may have noted that it was Pump #4. If so, remove the other 3 pumps.
Note on A133: My notes indicated 5 inline centrifugal pumps, although I have notes on only 3?
Note on E6: bc: Not Applicable
Note on F6: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on G6: bc: Moderate to high risk of failure.
Note on H6: bc: Visible degradation of equipment or structure, but acceptable.
Note on I6: bc: Well maintained, like new condition of equipment or structure.
Note on J6: bc: Not Applicable.
Note on K6: bc: Structure or equipment is not currently functioning for its intended use.
Note on L6: bc: Structure or equipment is in service but function is highly impaired.
Note on M6: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on N6: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on P6: bc: Not Applicable.
Note on Q6: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on Q68: No floor!
Note on R6: bc: Visible degradation of equipment or structure, but acceptable.
Note on S6: bc: Well maintained, like new condition of equipment or structure.
Note on T6: bc: Excessive
Note on U6: bc: High Life Cycle Costs but acceptable.
Note on V6: bc: Normal.
Note on AF6: bc: Not Applicable.
Note on AG6: bc: Structure or equipment integrity severely compromised by corrosion and/or wear. Moderate to high risk of imminent failure.
Note on AH6: bc: Visible degradation of equipment or structure, but acceptable.
Note on AI6: bc: Well maintained, like new condition of equipment or structure.
Note on AJ6: bc: Excessive
Note on AK6: bc: High Life Cycle Costs but acceptable.
Note on AL6: bc: Normal.
Note on AS5: bc: Pumps performing near rated capacity (+/- 5%)
Note on AU13: Packing used
Note on AV14: Packing used

## Buildings
Appendix 2A GWA Water Booster Stations - Buildings
|  | Booster Station Type |  |  |  | Condition and Functionality Rating | [9 empty] | Superstructure Building | [41 empty] | Wet Well | [19 empty] | Wet Well Ventilation |  |  |  | Dry Well Ventilation | [5 empty] | Hoist
Booster Station |  | Concrete Wet Well/ | Steel Dry Well/ | Self-Priming Pumps |  | General Condition Rating |  |  |  |  | General Functionality Rating |  |  |  |  | Exterior Wall Condition |  |  |  |  | Interior Wall Condition |  |  |  |  | Exterior Finish Condition |  |  |  |  | Interior Finish Condition |  |  |  |  | Equipment Finish Condition |  |  |  |  | Roof Condition |  |  |  |  | Window Condition |  |  |  |  | Pipe Support Condition |  |  |  |  | Equipment Access Layout OK |  | Top Slab Condition |  |  |  |  | Interior Wall Condition |  |  |  |  | Hatchway Condition |  |  |  |  | Hatchway Accessible |  |  |  |  | Mechanical Ventilation |  | Separate from Dry Well |  | Mechanical Ventilation |  | Gas Detection Equipment |  | Dehumidification Effective
| Building Name | Dry Well | Concrete Wet Well | Above Concrete Wet Well | In-line | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Yes | No | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Y | N | Y | N | Y | N | Y | N | Y | N | Y | N
Agana Heights (Ulloa Untalan) | none, litigation
Agat/Umatac | GPA Genset Bldg (no bldg for pump) |  |  |  | x | [50 empty] | nd |  |  | x | [29 empty] | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 0; Exterior Finish Condition 2; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 2; Pipe Support Condition 0
Santa Ana Upper | Booster Pump Bldg |  |  |  | x | [50 empty] | x | [32 empty] | x | no doors | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 1; Exterior Finish Condition 2; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2; Pipe Support Condition 2
Santa Ana Lower | Booster Pump Bldg |  |  |  | x | General Condition Rating 2: x; General Functionality Rating 2: x; Exterior Wall Condition 2: x; Interior Wall Condition 1: x; Exterior Finish Condition 1: x; Interior Finish Condition 1: x; Equipment Finish Condition 1: x; Roof Condition 2: x; Window Condition 3: x - hollow tile; Pipe Support Condition 1: x | x | [32 empty] | x | good doors, grafitti
Asan Spring (SECURED) | Booster Pump Bldg |  |  |  | x | [50 empty] | x | [33 empty] | front door poor | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2; Pipe Support Condition 2
Barrigada | none |  |  |  | x | [83 empty] | x
Chalan Palauan | none |  |  |  | x | [83 empty] | x
Mangenon Access Road | Booster Pump Bldg |  |  |  | x | [50 empty] | x | [32 empty] | x | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 3; Pipe Support Condition 1
Pago Bay | GPA Genset Bldg | [54 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3; Pipe Support Condition 0
| Booster Pump Shelter |  |  |  | x | [50 empty] | x | [32 empty] | x | bar: General Condition Rating 3; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 0; Pipe Support Condition 1
Ugum | no info
Northern | DID NOT VISIT
Wusstig | Abandoned
Malojloj (Malojloj Elevated) | Booster Pump Bldg |  |  |  | x | General Condition Rating 2: x; General Functionality Rating 2: x; Exterior Wall Condition 2: x; Interior Wall Condition 2: x; Exterior Finish Condition 2: x; Interior Finish Condition 2: x; Equipment Finish Condition 2: x; Roof Condition 2: x; Window Condition 3: x - hollow tile; Pipe Support Condition 2: x | x | [32 empty] | x | no door, also on site - office bldg (condition 1)
Malojloj Line Booster | Booster Pump Bldg |  |  |  | x | [50 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 2; Pipe Support Condition 0
| GPA Genset Bldg | [54 empty] | x | [32 empty] | x | No hoist - monorails are aligned with pumps | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 3; Interior Finish Condition 3; Equipment Finish Condition 2; Roof Condition 3; Window Condition 2; Pipe Support Condition 3
Latte Heights | Booster Pump Bldg |  |  |  | x | [50 empty] | x | [32 empty] | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 3; Exterior Finish Condition 2; Interior Finish Condition 3; Equipment Finish Condition 1; Roof Condition 3; Window Condition 2; Pipe Support Condition 2
Lower Pigua (Gayos) | GPA Genset Bldg | [54 empty] | nd | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 0; Exterior Finish Condition 1; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 2; Window Condition 2; Pipe Support Condition 0
| CL2 Bldg | [54 empty] | na | [33 empty] | no floor | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1; Pipe Support Condition 0
| Booster Pump Shelter |  |  |  | x | [50 empty] | x | [32 empty] | x | no walls | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 0; Interior Wall Condition 0; Exterior Finish Condition 0; Interior Finish Condition 0; Equipment Finish Condition 1; Roof Condition 2; Window Condition 0; Pipe Support Condition 1
Toguan | GPA Genset Bldg | [54 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 0; Exterior Finish Condition 2; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3; Pipe Support Condition 0
| Booster Pump Bldg |  |  |  | x | [50 empty] | x | [33 empty] | doors poor | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 2; Pipe Support Condition 2
Upper Pigua (Pigua) | Booster Pump Bldg |  |  |  | x | [50 empty] | x | [32 empty] | x | doors poor | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 1; Pipe Support Condition 3
Adawag | none - wood and chicken wire construction |  |  |  | x
Lower Nimitz Hill | none - concrete pad |  |  |  | x
Upper Nimitz Hill | SECURED
Santa Rita | Booster Pump Bldg |  |  | x | [51 empty] | x |  |  |  |  | x |  |  |  |  | x |  | x | [7 empty] | x |  |  | x | na |  | na |  | na |  | na |  |  | x | door poor | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 3; Roof Condition 2; Window Condition 2; Pipe Support Condition 2
| CL2 Bldg | [54 empty] | x | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1; Pipe Support Condition 0
| GPA Genset Bldg |  |  |  |  | General Condition Rating 3: x; General Functionality Rating 3: x; Exterior Wall Condition 2: x; Interior Wall Condition 0: nd; Exterior Finish Condition 2: x; Interior Finish Condition 0: nd; Equipment Finish Condition 0: nd; Roof Condition 3: x; Window Condition 3: x; Pipe Support Condition 0: na | nd
Sinifa | prv - did not visit
Truman | GPA Genset Bldg | [54 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 2; Pipe Support Condition 0
| Booster Pump Bldg |  |  |  | x | General Condition Rating 3: x; General Functionality Rating 3: x; Exterior Wall Condition 3: x; Interior Wall Condition 3: x; Exterior Finish Condition 3: x; Interior Finish Condition 3: x; Equipment Finish Condition 1: x; Roof Condition 3: x; Window Condition 2: x - hollow tile; Pipe Support Condition 1: x | x | [32 empty] | x | doors poor
Sinijana (Pale Kirin) | none - chain link enclosure with tin roof, tank and pump with pressure switch
Umatac #1 | Agat/Umatac
Umatac #2 | GPA Genset Bldg | [54 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 0; Exterior Finish Condition 2; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 2; Window Condition 2; Pipe Support Condition 0
| Booster Pump Bldg |  |  |  | x | General Condition Rating 3: x; General Functionality Rating 3: x; Exterior Wall Condition 2: x; Interior Wall Condition 1: x; Exterior Finish Condition 2: x; Interior Finish Condition 1: x; Equipment Finish Condition 1: x; Roof Condition 2: x; Window Condition 2: x - hollow tile; Pipe Support Condition 1: x | x | [32 empty] | x | doors poor
Umatac #3 | Toguan
Gayinero | Booster Pump Bldg |  |  |  | x | [50 empty] | x | [32 empty] | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2; Pipe Support Condition 2
Mataguac | Booster Pump Bldg |  |  |  | x | [50 empty] | x | [32 empty] | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 1; Pipe Support Condition 2
Santa Rosa | Booster Pump Bldg |  |  |  | x | [50 empty] | x | [32 empty] | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2; Pipe Support Condition 2
Yigo Elevated Tank | Booster Pump Bldg |  |  |  | x | [50 empty] | x | [32 empty] | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2; Pipe Support Condition 2
Brigade | GPA Genset Bldg | [54 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3; Pipe Support Condition 0
| Booster Pump Shelter |  |  |  | x | [50 empty] | x | [31 empty] | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 0; Pipe Support Condition 1
Camacho's | none - makeshift shelter with tin roof |  |  |  | x
Windward Hills | GPA Genset Bldg | [54 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3; Pipe Support Condition 0
| Booster Pump Bldg |  |  |  | x | [50 empty] | x | [33 empty] | makeshift (nice) plywood door | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2; Pipe Support Condition 2
Yona | SECURED
Note on G5: bc: Not Applicable
Note on H5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on I5: bc: Moderate to high risk of failure.
Note on J5: bc: Visible degradation of equipment or structure, but acceptable.
Note on K5: bc: Well maintained, like new condition of equipment or structure.
Note on L5: bc: Not Applicable.
Note on M5: bc: Structure or equipment is not currently functioning for its intended use.
Note on N5: bc: Structure or equipment is in service but function is highly impaired.
Note on O5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on P5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on Q5: bc: Not Applicable.
Note on R5: bc: Structure or equipment is not currently functioning for its intended use.
Note on S5: bc: Structure or equipment is in service but function is highly impaired.
Note on T5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on U5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on V5: bc: Not Applicable.
Note on W5: bc: Structure or equipment is not currently functioning for its intended use.
Note on X5: bc: Structure or equipment is in service but function is highly impaired.
Note on Y5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on Z5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AA5: bc: Not Applicable.
Note on AB5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AC5: bc: Structure or equipment is in service but function is highly impaired.
Note on AD5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AE5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AF5: bc: Not Applicable.
Note on AG5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AH5: bc: Structure or equipment is in service but function is highly impaired.
Note on AI5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AJ5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AK5: bc: Not Applicable.
Note on AL5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AM5: bc: Structure or equipment is in service but function is highly impaired.
Note on AN5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AO5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AP5: bc: Not Applicable.
Note on AQ5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AR5: bc: Structure or equipment is in service but function is highly impaired.
Note on AS5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AT5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AU5: bc: Not Applicable.
Note on AV5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AW5: bc: Structure or equipment is in service but function is highly impaired.
Note on AX5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AY5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AZ5: bc: Not Applicable.
Note on BA5: bc: Structure or equipment is not currently functioning for its intended use.
Note on BB5: bc: Structure or equipment is in service but function is highly impaired.
Note on BC5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BD5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on BE5: bc: Not Applicable.
Note on BF5: bc: Structure or equipment is not currently functioning for its intended use.
Note on BG5: bc: Not Applicable.
Note on BH5: bc: Structure or equipment is not currently functioning for its intended use.
Note on BI5: bc: Structure or equipment is in service but function is highly impaired.
Note on BJ5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BK5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on BL5: bc: Not Applicable.
Note on BM5: bc: Structure or equipment is not currently functioning for its intended use.
Note on BN5: bc: Structure or equipment is in service but function is highly impaired.
Note on BO5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BP5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on BQ5: bc: Not Applicable.
Note on BR5: bc: Structure or equipment is not currently functioning for its intended use.
Note on BS5: bc: Structure or equipment is in service but function is highly impaired.
Note on BT5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BU5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on BV5: bc: Not Applicable.
Note on BW5: bc: Structure or equipment is not currently functioning for its intended use.
Note on BX5: bc: Structure or equipment is in service but function is highly impaired.
Note on BY5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BZ5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.

## Generator
Appendix 2A GWA Water Booster Stations - Generators
[7 empty] | Condition and Functionality Rating | [9 empty] | Emergency Generator
Booster Station | Back-up Power |  | Emergency Generator |  |  |  | General Condition Rating |  |  |  |  | General Functionality Rating |  |  |  |  | Size |  | Fuel Tank |  | Spill Containment |  | Transfer Switch |  | Outdoor Panel
| None | Redundant Power | On-site | Portable | Automatic Start | Manual Start | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Y | N | Y | N | Y | N | Y | N | Y | N
Agana Heights (Ulloa Untalan) | x, litigation
Agat/Umatac |  | GPA
Santa Ana Upper | x
Santa Ana Lower | x
Asan Spring (SECURED) |  | x | x |  |  | x | [12 empty] | ext |  | x | bar: General Condition Rating 2; General Functionality Rating 2
Barrigada |  | GPA
Chalan Palauan | x
Mangenon Access Road |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | x | x |  |  |  | indoor tank with containment, standby barrel w/out containment | bar: General Condition Rating 3; General Functionality Rating 3
Pago Bay |  | GPA
Ugum |  | x | x |  |  | x | [10 empty] | x |  | x | bar: General Condition Rating 1; General Functionality Rating 0
Northern | at WWTP - did not assess
Wusstig | abandoned
Malojloj (Malojloj Elevated) |  | x | x |  |  | x | bar: General Condition Rating 1; General Functionality Rating 0
|  | x |  | x |  | x | bar: General Condition Rating 2; General Functionality Rating 3
Malojloj Line Booster |  | GPA
Latte Heights |  | GPA
Lower Pigua (Gayos) |  | GPA
Toguan |  | GPA
Upper Pigua (Pigua) | x
Adawag | x
Lower Nimitz Hill | x
Upper Nimitz Hill | SECURED
Santa Rita |  | GPA
Sinifa | prv | GPA
Truman |  | GPA
Sinijana (Pale Kirin) | x
Umatac #1 | Agat/Umatac
Umatac #2 |  | GPA
Umatac #3 | Toguan
Gayinero | x
Mataguac |  | x | x |  |  | x | [12 empty] | x - indoor day tank and external tank |  | x - yes for outdoor tank, no on indoor tank | bar: General Condition Rating 3; General Functionality Rating 3
Santa Rosa |  | GPA
Yigo Elevated Tank |  | x | x |  |  | x | bar: General Condition Rating 1; General Functionality Rating 0
Brigade |  | GPA
Camacho's | x
Windward Hills |  | GPA
Yona | SECURED
Note on H5: bc: Not Applicable
Note on I5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on J5: bc: Moderate to high risk of failure.
Note on K5: bc: Visible degradation of equipment or structure, but acceptable.
Note on L5: bc: Well maintained, like new condition of equipment or structure.
Note on M5: bc: Not Applicable.
Note on N5: bc: Structure or equipment is not currently functioning for its intended use.
Note on O5: bc: Structure or equipment is in service but function is highly impaired.
Note on P5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on Q5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on R4: bc: Generator size sufficient for pumps and auxiliary equipment.
Note on T4: bc: Fuel tank sized for 24-hour operation.
Note on V4: bc: Fuel spill containment provisions.
Note on X4: bc: Outdoor panel location area satisfactory for portable generator.
Note on Z4: bc: Transfer switch condition satisfactory.