## Equipment
Appendix 2A GWA Wells - Equipment
|  |  |  | Condition and Functionality Rating | [9 empty] | Motor | [7 empty] | Pump | [11 empty] | CHLORINATION SYSTEM
Well | Equipment Name | Asset Class | Asset Number | Physical Condition Rating |  |  |  |  | Functionality Rating |  |  |  |  | Vibration |  | Temperature |  | High Efficiency |  | Power Factor Correction |  | Vibration |  | Cavitation |  | Temperature |  | Pump Performing |  | Seals Functional |  | Seal Water System Functional |  | CL2 Pump | CL2 Pump Base | Chlorinator | CL2 Scale
|  |  |  | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Excessive | Normal | Excessive | Normal | Excessive | Normal | Yes | No | Yes | No | Yes | No | 0-4 | 0-3 | 0-4 | 0-4
A1 | Out of service - secured - pullout | bar: Functionality Rating 1
A2 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 2 | 3 | bar: Physical Condition Rating 2; Functionality Rating 2
A3 | Out of service - secured - pullout | bar: Functionality Rating 1
A4 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 3 | 0 | bar: Physical Condition Rating 3; Functionality Rating 3
A5 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 1 | 3 | 1 | bar: Physical Condition Rating 2; Functionality Rating 2
A6 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 0 | 2 | 2 | bar: Physical Condition Rating 2; Functionality Rating 1
A7 | Hard broke | bar: Functionality Rating 1
A8 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x | x |  | x |  |  | x | x |  | x |  | x |  | 2 | 0 | 1 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
A9 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 2 | 3 | bar: Physical Condition Rating 2; Functionality Rating 2
A10 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 2 | 3 | 0 | bar: Physical Condition Rating 3; Functionality Rating 3
A12 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 0 | 2 | 3 |  | 1 | bar: Physical Condition Rating 1; Functionality Rating 2
A13 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 2 | 3 | bar: Physical Condition Rating 2; Functionality Rating 2
A14 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x | x |  | x |  |  | x | x |  | x |  | x |  | 1 | 1 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
A15 | Submersible Pump | [13 empty] | na |  | na |  | na |  | na |  | na |  | na |  | na |  | x |  | na |  | na | 2 | 0 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 1
A17 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x | x |  | x |  |  | x | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 2
A18 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 2 | 3 | bar: Physical Condition Rating 2; Functionality Rating 2
A19 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 2 | 2 | 0 | bar: Physical Condition Rating 2; Functionality Rating 3
A21 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x | x |  | x |  |  | x | x |  | x |  | x |  | 1 | 2 | 2 | 3 | bar: Physical Condition Rating 1; Functionality Rating 2
A23
A25 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 2 | 2 | 3 | bar: Physical Condition Rating 1; Functionality Rating 2
A26 | Hard broke | bar: Functionality Rating 1
A28 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 1 | 2 | 0 | wood CL2 pump base | bar: Physical Condition Rating 1; Functionality Rating 1
A29 | ?
A30 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | x |  | x | bar: Physical Condition Rating 2; Functionality Rating 3
A31 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 2 | 3 | 3 | bar: Physical Condition Rating 1; Functionality Rating 2
A32 | Hard broke | [13 empty] | na |  | na |  | na |  | na |  | na |  | na |  | na |  | x |  | na |  | na | na | 2 | 2 | 0 | bar: Functionality Rating 1
Y-1 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 0 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
Y-2 - offline - failed - motor bad | Submersible Pump | [32 empty] | no cl2 injection, same line as Y-1 | bar: Physical Condition Rating 1; Functionality Rating 1
Y-3 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x | x |  | x |  |  | x | x |  | x |  | x |  | 3 | 0 | 1,1 | nd | chlorinators high vibration | bar: Physical Condition Rating 1; Functionality Rating 2
Y-4 | Hard broke since mid-80s | bar: Functionality Rating 1
Y-5 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 0 | 3 | 1 | bar: Physical Condition Rating 1; Functionality Rating 2
Y-6 | Submersible Pump | [12 empty] | x |  | x |  |  | x |  | x | x |  |  | x | x |  | x |  | x |  | x |  | 3 | 0 | 3 | 1 | frequent repair needed on sub pump/motor | bar: Physical Condition Rating 1; Functionality Rating 1
Y-7 | Secured - Hardbroke | bar: Functionality Rating 1
Y-9 | Submersible Pump | [32 empty] | 3 | nd | 3 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
Y-10 | Pump | [13 empty] | x |  | x |  | x |  |  |  | x | x |  |  | x | x |  | x |  | x |  | 3 | 2 | 3 | 1 | bar: Physical Condition Rating 2; Functionality Rating 2
Y-12 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 0 | 3 | 1 | bar: Physical Condition Rating 2; Functionality Rating 2
Y-14 | Hard broke since mid-80s | bar: Functionality Rating 1
Y-15 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | nd | 2 | 2 | bar: Physical Condition Rating 3; Functionality Rating 3
Y-16 | Inline pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 2 | 3 | 0 | bar: Physical Condition Rating 3; Functionality Rating 3
Y-17 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 3 | 2 | 1 | bar: Physical Condition Rating 2; Functionality Rating 2
Y-21A | Inline pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 2 | 3 | 0 | bar: Physical Condition Rating 3; Functionality Rating 3
Y-23 - offline | Submersible Pump | [32 empty] | 1 | nd | 1 | 1 | bar: Physical Condition Rating 1; Functionality Rating 1
D-1 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 2 | 2 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
D-2 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | na | na | na | na | no CL2 | bar: Physical Condition Rating 1; Functionality Rating 2
D-3 | Hard broke | bar: Functionality Rating 1
D-4 - Secured | Submersible Pump | bar: Functionality Rating 1
D-5 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 2 | 3 | 0 | bar: Physical Condition Rating 3; Functionality Rating 3
D-6 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 1 | 1 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
D-7 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 0 | 0 | 0 | 0 | bar: Physical Condition Rating 3; Functionality Rating 3
D-8 | Secured | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Functionality Rating 3
D-9 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 0 | 0 | 0 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
D-10 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
D-11 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 1 | 1 | 1 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
D-12 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
D-13 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x | x |  |  | x | x |  | x |  | x |  | 3 | 0 | 3 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
D-14 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 3; Functionality Rating 3
D-15 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 3 | 3 | 0 | bar: Physical Condition Rating 3; Functionality Rating 3
D-16 - Secured | Submersible Pump | bar: Functionality Rating 1
D-17 - Hard broke | bar: Functionality Rating 1
D-18 - Hard broke | bar: Functionality Rating 1
D-19 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x | x |  |  | x | x |  | x |  | x |  | 3 | 2 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
D-20 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 1 | 3 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
D-21 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 0 | 2 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
D-22 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 0 | 0 | 0 | 0 | bar: Physical Condition Rating 2; Functionality Rating 3
D-24 | Hard broke-secured | bar: Functionality Rating 1
F-1 | Secured for pullout | bar: Functionality Rating 1
F-2 | Submersible pump | [13 empty] | x |  | x |  | x |  | x | x |  | x |  |  | x | x |  | x |  | x |  | 2 | 1 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
F-3 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 2 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
F-4 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
F-5 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x | x |  |  | x | x |  | x |  | x |  | 1 | 0 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 1
F-6 | Pump | [13 empty] | x |  | x |  | x |  | x | x |  |  | x |  | x | x |  | x |  | x |  | 1 | 1 | 2 | 3 | bar: Physical Condition Rating 1; Functionality Rating 1
F-7 | Submersible pump | [13 empty] | na |  | na |  | na |  | na |  | na |  | na |  | na |  | x | na |  | na |  | 0 | 0 | 0 | 0 | bar: Physical Condition Rating 1; Functionality Rating 1
F-8 | Secured | bar: Functionality Rating 1
F-9 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 2 | 3 | 4 | bar: Physical Condition Rating 2; Functionality Rating 3
F-10 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 3 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
F-11 | Submersible pump | [13 empty] | x |  | x |  | x |  | x | x |  |  | x |  | x | x |  | x |  | x |  | 2 | 2 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
F-12 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 2 | 3 | 0 | bar: Physical Condition Rating 2; Functionality Rating 3
F-13 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 0 | 3 | 3 | bar: Physical Condition Rating 2; Functionality Rating 2
F-15 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 0 | 0 | 0 | 0 | bar: Physical Condition Rating 2; Functionality Rating 3
F-16 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 3 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
F-17 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 3 | 2 | 2 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
F-18 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 2 | 3 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
G-501 | Pump | [13 empty] | x | x |  |  | x |  | x |  | x | x |  |  | x | x |  | x |  | x |  | 2 | 1 | 1 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
Ag-1A | Inline | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 0 | 2 | 0 | bar: Physical Condition Rating 3; Functionality Rating 3
Ag-2A | Inline | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 2 | 0 | bar: Physical Condition Rating 3; Functionality Rating 3
H-1 | Pump | [13 empty] | x | x |  |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 2
HGC-2 | Inline | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 1 | 0 | 2 | 3 | bar: Physical Condition Rating 2; Functionality Rating 3
M-1 | ? | bar: Functionality Rating 0
M-2 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x | x |  |  | x | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 2
M-3 | Submersible pump | [13 empty] | x |  | x |  | x |  | x | x |  | x |  |  | x | x |  | x |  | x |  | 0 | 0 | 0 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
M-4 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 2
M-5 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 1 | 1 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
M-6 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 2 | 3 | 3 | bar: Physical Condition Rating 1; Functionality Rating 2
M-7 | Secured for pullout | bar: Functionality Rating 1
M-8 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 2
M-9 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 1 | 1 | 2 | 0 | bar: Physical Condition Rating 1; Functionality Rating 2
M-12 | Pump | [13 empty] | x | x |  |  | x |  | x |  | x | x |  |  | x | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 1
M-14 | Secured | bar: Functionality Rating 1
M-15 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 2 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
M-17A | Hard broke | bar: Functionality Rating 1
M-17B | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 1 | 1 | 2 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
M-18 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 3 | 3 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
M-20A | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 1 | 2 | 0 | bar: Physical Condition Rating 2; Functionality Rating 2
M-21 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 2 | 3 | 3 | 0 | bar: Physical Condition Rating 2; Functionality Rating 3
M-23 | Submersible pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 1 | 1 | 2 | 0 | bar: Physical Condition Rating 2; Functionality Rating 3
MJ-1 | Secured | bar: Functionality Rating 1
MJ-5 | Secured | bar: Functionality Rating 1
EX-5 | Submersible Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x |  | 1 | 0 | 2 | 0 | plants growing out of chlorine pump | bar: Physical Condition Rating 2; Functionality Rating 2
EX-11 | Pump | [13 empty] | x |  | x |  | x |  | x |  | x |  | x |  | x | x |  | x |  | x | bar: Physical Condition Rating 1; Functionality Rating 2
NAS-1 | Secured | bar: Functionality Rating 1
Note on A9: Piping needs repair/replacing
Note on A24: Did not visit. Too dangerous ingress.
Note on A30: Well head not sealed.
Note on A31: Well is out of service
Note on A81: Not in service since Jan05
Note on A96: Old well station
Note on A99: Older well
Note on A101: Older well
Note on A105: Older well
Note on A107: Severe cavitation, sucking air
Note on B54: Motor burnt
Note on B95: Pump recently pulled
Note on B114: Mean Time between repairs: 1
Note on E5: bc: Not Applicable
Note on F5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on G5: bc: Moderate to high risk of failure.
Note on H5: bc: Visible degradation of equipment or structure, but acceptable.
Note on I5: bc: Well maintained, like new condition of equipment or structure.
Note on J5: bc: Not Applicable.
Note on K5: bc: Structure or equipment is not currently functioning for its intended use.
Note on L5: bc: Structure or equipment is in service but function is highly impaired.
Note on M5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on N5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AC4: bc: Pumps performing near rated capacity (+/- 5%)
Note on AK47: 2-station chlorinator, but no auto switchover
Note on AK65: 2-station chlorinator with manual switchover
Note on AL83: Scale works!
Note on AL87: Scale works!

## Buildings
Appendix 2A GWA Wells - Buildings
|  | Condition and Functionality Rating | [9 empty] | Superstructure Building | [36 empty] | Wellhead
Well |  | General Condition Rating |  |  |  |  | General Functionality Rating |  |  |  |  | Exterior Wall Condition |  |  |  |  | Interior Wall Condition |  |  |  |  | Exterior Finish Condition |  |  |  |  | Interior Finish Condition |  |  |  |  | Equipment Finish Condition |  |  |  |  | Roof Condition |  |  |  |  | Window Condition |  |  |  |  | Equipment Access Layout OK |  | Top Block Condition |  |  |  |  | Flange Condition |  |  |  |  | Pipe/Valve Condition |  |  |  |  | Pipe/Valve Bases
| Building Name | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Yes | No | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3
A1 | Out of service - secured - pullout
A2 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
A3 | Out of service - secured - pullout
A4 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 2
A5 | Chlorine Bldg | [45 empty] | x | [20 empty] | wooden walls, tin roof | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 0
| Pump Enclosure | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 0; Window Condition 0
| GPA Generator Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
A6 | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 3; Roof Condition 1; Window Condition 1
| GPA Generator Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
A7 | Hardbroke
A8 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x | [5 empty] | x | [5 empty] | x |  |  |  | x |  | large station, also booster pumps but not working | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
A9 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
A10 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 2
A12 | Chlorine Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 3; Roof Condition 2; Window Condition 2
| GPA Generator Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
A13 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
A14 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  | chlorine door very poor | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 3; Interior Finish Condition 3; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
A15 | Chlorine Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 3; Roof Condition 2; Window Condition 2
A17 | Chlorine Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
| GPA Generator Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
A18 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
A19 | Chlorine Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
A21 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
A23 | supposed to be same as A-25
A25 | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 3; Roof Condition 2; Window Condition 2
| GPA Generator Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 0; Exterior Finish Condition 2; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 2
A26 | Hardbroke
A28 | Chlorine Bldg | [46 empty] | x | [19 empty] | all 4 walls held together by chain wrapped around | bar: General Condition Rating 1; General Functionality Rating 0; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
| Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x | [5 empty] | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
A29 | ?
A30 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
A31 | Chlorine Bldg | [45 empty] | x |  |  | x | [6 empty] | x |  |  |  |  | x |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 3; Roof Condition 2; Window Condition 2
| GPA Generator Bldg | [45 empty] | nd | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 0; Exterior Finish Condition 2; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 2
A32 | Hardbroke
Y-1 | CL2 Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
Y-2 - offline - failed - motor bad | Northern Storage Site (CL2) | [45 empty] | na |  | nd |  |  |  |  | nd |  |  |  |  | nd |  |  |  |  | nd |  |  |  | no security! | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
Y-3 | Chlorine and Generator Bldg | [45 empty] | x |  | nd |  |  |  |  | nd |  |  |  |  | nd |  |  |  |  | nd | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
Y-4 | Hard broke since mid-80s
Y-5 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
Y-6 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
Y-7 | Secured - Hardbroke
Y-9 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
Y-10 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
Y-12 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
Y-14 | Hard broke since mid-80s
Y-15 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  | x | [5 empty] | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
Y-16 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 3; Interior Finish Condition 3; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
Y-17 | Chlorine and Generator Bldg | [45 empty] | x |  | nd |  |  |  |  | nd |  |  |  |  | nd |  |  |  |  | nd | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
Y-21A | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 3; Interior Finish Condition 3; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
Y-23 - offline | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
D-1 | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
D-2 | GPA Genset Bldg | [45 empty] | nd |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
D-3 | Hardbroke, disconnected
D-4 - Secured | Secured
D-5 | GPA Genset Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
D-6 | Chlorine Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 1
D-7 | GPA Genset Bldg | [45 empty] | nd |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
D-8 | Secured
D-9 | GPA Genset Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
D-10 | GPA Genset Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
D-11 | GPA Genset Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
D-12 | GPA Genset Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  | fence very poor | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
D-13 | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x | [5 empty] | x |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 1; Window Condition 2
D-14 | GPA Genset Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
D-15 | Chlorine Bldg | [45 empty] | x |  |  |  |  | x |  |  |  | x |  |  |  |  | x | [5 empty] | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 2; Interior Finish Condition 2; Equipment Finish Condition 3; Roof Condition 2
D-16 - Secured
D-17 - Hard broke
D-18 - Hard broke
D-19 | Chlorine Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 1; Window Condition 2
D-20 | Chlorine Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 1; Window Condition 2
D-21 | Chlorine Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 1; Window Condition 2
D-22 | Chlorine Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 2
D-24 | Hardbroke, secured
F-1 | secured
F-2 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
F-3 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
F-4 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
F-5 | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
| GPA Genset Bldg | [45 empty] | nd | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 0; Exterior Finish Condition 1; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 2; Window Condition 2
F-6 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 1; Exterior Finish Condition 2; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 2; Window Condition 3
F-7 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 2
F-8 | secured
F-9 | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
| GPA Genset Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
F-10 | Chlorine Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x |  |  | no doors | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 1; Window Condition 1
| GPA Genset Bldg | [45 empty] | nd | [20 empty] | door poor | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 0; Exterior Finish Condition 2; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 2; Window Condition 2
F-11 | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  | door poor | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 1
| GPA Genset Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 0; Exterior Finish Condition 2; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 2
F-12 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 1; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 3
F-13 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  | no doors | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 3; Roof Condition 3; Window Condition 2
F-15 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x |  |  | no door on cl room | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
F-16 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
F-17 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
F-18 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
G-501 | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
| GPA Genset Bldg | [45 empty] | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
Ag-1A | Chlorine Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 3; Interior Finish Condition 3; Equipment Finish Condition 3; Roof Condition 3; Window Condition 3
| GPA Genset Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
Ag-2A | Chlorine Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 3; Interior Finish Condition 3; Equipment Finish Condition 3; Roof Condition 3; Window Condition 3
| GPA Genset Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
H-1 | no info
HGC-2 | Chlorine Bldg | General Condition Rating 2: x; General Functionality Rating 1: x; Exterior Wall Condition 0: no walls; Interior Wall Condition 0: na; Exterior Finish Condition 0: na; Interior Finish Condition 0: na; Equipment Finish Condition 2: x; Roof Condition 2: x; Window Condition 0: na | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  | no walls - equipment exposed
M-1 | ?
M-2 | no info
M-3 | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
| GPA Genset Bldg | [45 empty] | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 2; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 2
M-4 | no info
M-5 | no bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  | same site as M15, share genset/bldg, chlorination out in open, no caulking/seal at wellhead base/flange | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 0; Interior Wall Condition 0; Exterior Finish Condition 0; Interior Finish Condition 0; Equipment Finish Condition 1; Roof Condition 0; Window Condition 0
M-6 | Chlorine Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 1; Window Condition 1
| GPA Genset Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 3; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 3
M-7 | secured for pullout
M-8 | no info
M-9 | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
| GPA Genset Bldg | [45 empty] | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 0; Exterior Finish Condition 2; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 2
M-12 | no info
M-14 | Secured
M-15 | Chlorine Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 1; Window Condition 1
| GPA Genset Bldg | [45 empty] | nd | bar: General Condition Rating 2; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 0; Exterior Finish Condition 1; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 2; Window Condition 2
M-17A | Hardbroke - all 1 | [66 empty] | chlorine bldg, genset bldg all poor (1)
M-17B | Chlorine Bldg | [45 empty] | x |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 1; General Functionality Rating 2; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 1
| GPA Genset Bldg | [45 empty] | nd | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 2; Interior Wall Condition 0; Exterior Finish Condition 2; Interior Finish Condition 0; Equipment Finish Condition 0; Roof Condition 3; Window Condition 2
M-18 | Chlorine and Generator Bldg | [45 empty] | x |  |  | x | [5 empty] | x |  |  |  |  | x |  |  |  | x |  |  | doors poor | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 3; Interior Finish Condition 2; Equipment Finish Condition 2; Roof Condition 3; Window Condition 2
M-20A | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
M-21 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  | doors poor | bar: General Condition Rating 2; General Functionality Rating 2; Exterior Wall Condition 2; Interior Wall Condition 2; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 2; Roof Condition 2; Window Condition 2
M-23 | Chlorine and Generator Bldg | [45 empty] | x |  |  |  |  | x |  |  |  | x |  |  |  |  | x | [5 empty] | x | bar: General Condition Rating 3; General Functionality Rating 3; Exterior Wall Condition 3; Interior Wall Condition 3; Exterior Finish Condition 3; Interior Finish Condition 3; Equipment Finish Condition 2; Roof Condition 3; Window Condition 3
MJ-1 | Secured
MJ-5 | Secured
EX-5 | Chlorine Bldg | [45 empty] | x |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  |  |  |  | x |  | plants growing out of chlorine pump | bar: General Condition Rating 1; General Functionality Rating 1; Exterior Wall Condition 1; Interior Wall Condition 1; Exterior Finish Condition 1; Interior Finish Condition 1; Equipment Finish Condition 1; Roof Condition 1; Window Condition 1
EX-11 | no info
NAS-1 | Secured
Note on A9: Piping needs repair/replacing
Note on A29: Did not visit. Too dangerous ingress.
Note on A37: Well head not sealed.
Note on A39: Well is out of service
Note on A90: Not in service since Jan05
Note on A111: Old well station
Note on A114: Older well
Note on A117: Older well
Note on A122: Older well
Note on A125: Severe cavitation, sucking air
Note on C5: bc: Not Applicable
Note on D5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on E5: bc: Moderate to high risk of failure.
Note on F5: bc: Visible degradation of equipment or structure, but acceptable.
Note on G5: bc: Well maintained, like new condition of equipment or structure.
Note on H5: bc: Not Applicable.
Note on I5: bc: Structure or equipment is not currently functioning for its intended use.
Note on J5: bc: Structure or equipment is in service but function is highly impaired.
Note on K5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on L5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on M5: bc: Not Applicable.
Note on N5: bc: Structure or equipment is not currently functioning for its intended use.
Note on O5: bc: Structure or equipment is in service but function is highly impaired.
Note on P5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on Q5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on R5: bc: Not Applicable.
Note on S5: bc: Structure or equipment is not currently functioning for its intended use.
Note on T5: bc: Structure or equipment is in service but function is highly impaired.
Note on U5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on V5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on W5: bc: Not Applicable.
Note on X5: bc: Structure or equipment is not currently functioning for its intended use.
Note on Y5: bc: Structure or equipment is in service but function is highly impaired.
Note on Z5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AA5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AB5: bc: Not Applicable.
Note on AC5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AD5: bc: Structure or equipment is in service but function is highly impaired.
Note on AE5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AF5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AG5: bc: Not Applicable.
Note on AH5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AI5: bc: Structure or equipment is in service but function is highly impaired.
Note on AJ5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AK5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AL5: bc: Not Applicable.
Note on AM5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AN5: bc: Structure or equipment is in service but function is highly impaired.
Note on AO5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AP5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AQ5: bc: Not Applicable.
Note on AR5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AS5: bc: Structure or equipment is in service but function is highly impaired.
Note on AT5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on AU5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on AV5: bc: Not Applicable.
Note on AW5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AX5: bc: Not Applicable.
Note on AY5: bc: Structure or equipment is not currently functioning for its intended use.
Note on AZ5: bc: Structure or equipment is in service but function is highly impaired.
Note on BA5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BB5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on BC5: bc: Not Applicable.
Note on BD5: bc: Structure or equipment is not currently functioning for its intended use.
Note on BE5: bc: Structure or equipment is in service but function is highly impaired.
Note on BF5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BG5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on BH5: bc: Not Applicable.
Note on BI5: bc: Structure or equipment is not currently functioning for its intended use.
Note on BJ5: bc: Structure or equipment is in service but function is highly impaired.
Note on BK5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on BL5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on BM5: bc: Not Applicable.
Note on BN5: bc: Structure or equipment is not currently functioning for its intended use.
Note on BO5: bc: Structure or equipment is in service but function is highly impaired.
Note on BP5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.

## Generator
Appendix 2A GWA Wells - Generators
[7 empty] | Condition and Functionality Rating | [9 empty] | Emergency Generator
Well | Back-up Power |  | Emergency Generator |  |  |  | General Condition Rating |  |  |  |  | General Functionality Rating |  |  |  |  | Size |  | Fuel Tank |  | Spill Containment |  | Transfer Switch |  | Outdoor Panel
| None | Redundant Power | On-site | Portable | Automatic Start | Manual Start | 0 | 1 | 2 | 3 | 4 | 0 | 1 | 2 | 3 | 4 | Y | N | Y | N | Y | N | Y | N | Y | N
A1 | Out of service - secured - pullout | bar: General Condition Rating 0
A2 |  | GPA
A3 | Out of service - secured - pullout | bar: General Condition Rating 0
A4 |  | GPA
A5 |  | GPA
A6 |  | GPA
A7 | Hardbroke | bar: General Condition Rating 0
A8 |  | GPA
A9 |  | GPA
A10 |  | GPA
A12 |  | GPA
A13 |  | GPA
A14 |  | GPA
A15 |  | GPA
A17 |  | GPA
A18 |  | GPA
A19 |  | GPA
A21 |  | GPA
A23 |  | GPA
A25 |  | GPA
A26 | Hardbroke | bar: General Condition Rating 0
A28 |  | GPA
A29 | ? | GPA
A30 |  | x | x |  | x | [11 empty] | x |  | x |  | x | bar: General Condition Rating 2; General Functionality Rating 2
A31 |  | GPA
A32 | Hardbroke | bar: General Condition Rating 0
Y-1 |  | GPA
Y-2 - offline - failed - motor bad |  | GPA
Y-3 |  | GPA
Y-4 | Hard broke since mid-80s | bar: General Condition Rating 0; General Functionality Rating 0
Y-5 |  | GPA
Y-6 |  | GPA
Y-7 | Secured | bar: General Condition Rating 0; General Functionality Rating 0
Y-9 |  | GPA
Y-10 |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | bar: General Condition Rating 3; General Functionality Rating 3
Y-12 |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | bar: General Condition Rating 3; General Functionality Rating 3
Y-14 | Hard broke since mid-80s | bar: General Condition Rating 0; General Functionality Rating 0
Y-15 |  | x | x |  | x | [11 empty] | x |  | x |  | x | bar: General Condition Rating 4; General Functionality Rating 4
Y-16 |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | bar: General Condition Rating 3; General Functionality Rating 3
Y-17 |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | bar: General Condition Rating 2; General Functionality Rating 2
Y-21A |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | bar: General Condition Rating 3; General Functionality Rating 3
Y-23 - offline |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | bar: General Condition Rating 4 to General Functionality Rating 0
D-1 | x
D-2 |  | GPA
D-3 | hardbroke, disconnected | bar: General Condition Rating 0; General Functionality Rating 1
D-4 - Secured | Secured | bar: General Condition Rating 0; General Functionality Rating 1
D-5 |  | GPA
D-6 |  | GPA
D-7 |  | GPA
D-8 | Secured | bar: General Condition Rating 0; General Functionality Rating 1
D-9 |  | GPA
D-10 |  | GPA
D-11 |  | GPA
D-12 |  | GPA
D-13 |  | GPA
D-14 |  | GPA
D-15 |  | GPA
D-16 - Secured | bar: General Condition Rating 0; General Functionality Rating 1
D-17 - Hard broke | bar: General Condition Rating 0; General Functionality Rating 1
D-18 - Hard broke | bar: General Condition Rating 0; General Functionality Rating 1
D-19 |  | GPA
D-20 |  | GPA
D-21 |  | GPA
D-22 |  | GPA
D-24 | Hardbroke, secured | bar: General Condition Rating 0; General Functionality Rating 1
F-1 | secured | bar: General Condition Rating 0
F-2 |  | GPA
F-3 |  | GPA
F-4 |  | GPA
F-5 |  | GPA
F-6 |  | GPA
F-7 |  | GPA
F-8 | secured | bar: General Condition Rating 0
F-9 |  | GPA
F-10 |  | GPA
F-11 |  | GPA
F-12 |  | GPA
F-13 |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | bar: General Condition Rating 3; General Functionality Rating 3
F-15 |  | GPA
F-16 |  | ?
F-17 |  | ?
F-18 |  | ?
G-501 |  | GPA
Ag-1A |  | GPA
Ag-2A |  | GPA
H-1 |  | GPA
HGC-2 | x
M-1 |  | GPA
M-2 |  | GPA
M-3 |  | GPA
M-4 |  | GPA
M-5 |  | GPA - shared with M15
M-6 |  | GPA
M-7 | secured for pullout | bar: General Condition Rating 0
M-8 |  | GPA
M-9 |  | GPA
M-12 |  | GPA
M-14 | Secured | bar: General Condition Rating 0
M-15 |  | GPA - shared with M5
M-17A | hardbroke | bar: General Condition Rating 0
M-17B |  | GPA
M-18 |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | bar: General Condition Rating 3; General Functionality Rating 3
M-20A |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | bar: General Condition Rating 2; General Functionality Rating 2
M-21 |  | GIAA - Airport
M-23 |  | x | x |  |  | x | [10 empty] | x |  | x |  | x | bar: General Condition Rating 3; General Functionality Rating 3
MJ-1 | Secured | bar: General Condition Rating 0
MJ-5 | Secured | bar: General Condition Rating 0
EX-5 |  | GPA
EX-11 |  | GPA
NAS-1 | Secured | bar: General Condition Rating 0
Note on A9: Piping needs repair/replacing
Note on A24: Did not visit. Too dangerous ingress.
Note on A30: Well head not sealed.
Note on A31: Well is out of service
Note on A81: Not in service since Jan05
Note on A96: Old well station
Note on A99: Older well
Note on A101: Older well
Note on A105: Older well
Note on A107: Severe cavitation, sucking air
Note on H5: bc: Not Applicable
Note on I5: bc: Structure or equipment integrity severely compromised by corrosion and/or wear.
Note on J5: bc: Moderate to high risk of failure.
Note on K5: bc: Visible degradation of equipment or structure, but acceptable.
Note on L5: bc: Well maintained, like new condition of equipment or structure.
Note on M5: bc: Not Applicable.
Note on N5: bc: Structure or equipment is not currently functioning for its intended use.
Note on O5: bc: Structure or equipment is in service but function is highly impaired.
Note on P5: bc: Structure or equipment is in service but maintenance or operational requirements substantially exceed that expected for this asset class.
Note on Q5: bc: Structure or equipment functions as intended, maintenance tasks and frequencies as expected for this asset class.
Note on R4: bc: Generator size sufficient for pumps and auxiliary equipment.
Note on T4: bc: Fuel tank sized for 24-hour operation.
Note on V4: bc: Fuel spill containment provisions.
Note on X4: bc: Outdoor panel location area satisfactory for portable generator.
Note on Z4: bc: Transfer switch condition satisfactory.